## Stations
ID | Power Plant | Owner/Operator | Main Power Producer | Vested (2004) | Vested (LNG) | Commissioned | Registration Status | Registered Capacity [MW] | Technology | Fuel | Fuel ID* | Cooling System | Stack height [m] | Condenser exhaust height [m] | Unit Name | Units | lat (°) | long (°) | Comments | More info
0 | Senoko Power Station | Senoko Energy Pte Ltd | Y | Y |  | 2012 | GRF | 862 | CCGT | nat gas | LNG (JKM) | once-through | 100 | 0 | SNK CCP 6, 7 |  | 1.4647 | 103.7974 | Various stages were commissioned in different years. Latest 2x 425 MW borne out of LNG Vesting
1 | Senoko Power Station | Senoko Energy Pte Ltd | Y | Y |  | 2004 | GRF | 730 | CCGT | nat gas | PNG (HH) | once-through | 100 | 0 | SNK CCP 4, 5 |  | 1.4647 | 103.7974
2 | Senoko Power Station | Senoko Energy Pte Ltd | Y | Y |  | 2002 | GRF | 365 | CCGT | nat gas | PNG (HH) | once-through | 100 | 0 | SNK CCP 3 |  | 1.4647 | 103.7974
3 | Senoko Power Station | Senoko Energy Pte Ltd | Y | Y |  | 1996 | GRF | 850 | CCGT | nat gas | PNG (HH) | once-through | 100 | 0 | SNK CCP 1, 2 |  | 1.4647 | 103.7974
4 | Senoko Power Station | Senoko Energy Pte Ltd | Y | Y |  |  | GRF | 493 | Oil-fired ST | crude oil | Crude (Dubai) | once-through | 100 | 0 | SNK OilST |  | 1.4647 | 103.7974 | Oil ST is just backup.
5 | Pulau Seraya Power Station | YTL PowerSeraya Pte Ltd | Y | Y |  | 2010 | GRF | 740 | Cogen CCGT | nat gas | LNG (JKM) | BP-cogen | 100 |  | PulSer CCP3, 4 |  | 1.2803 | 103.7259 | 800 MW but only 2x370MW registered
6 | Pulau Seraya Power Station | YTL PowerSeraya Pte Ltd | Y | Y |  | 2002 | GRF | 732 | CCGT | nat gas | PNG (HH) | once-through | 100 | 0 | PulSer CCP1, 2 |  | 1.2803 | 103.7259 | There were plans of converting these two to co-gen, but "Media Resource" page listed 2x cogen CCGT and 2x CCGT only.
7 | Pulau Seraya Power Station | YTL PowerSeraya Pte Ltd | Y | Y |  |  | GRF | 724 | Oil-fired ST | Orimulsion | Crude (Dubai) | once-through | 100 | 0 | PulSer OilST1 | 3x 250 MW | 1.2793 | 103.7269 | Scale all Oil-fired ST by 1448 MW licensed / 1500 MW actual
8 | Pulau Seraya Power Station | YTL PowerSeraya Pte Ltd | Y | Y |  |  | GRF | 724 | Oil-fired ST | heavy fuel oil | Crude (Brent) | once-through | 100 | 0 | PulSer OilST2 | 3x 250 MW | 1.2781 | 103.7286
9 | Jurong Power Station | YTL PowerSeraya Pte Ltd | Y | Y |  |  | GRF | 180 | OCGT | diesel | Crude (WTI) | once-through | 100 | 0 | JRNG OCGT | 2x 105 MW | 1.3113 | 103.7108 | Wikipedia says capacity is 180 MW/210 MW; thus, remaining unmapped 3x250 MW oil ST at Pulau
10 | Tuas Power Station | Tuas Power Generation Pte Ltd | Y | Y |  | 2014 | GRF | 405.9 | Cogen CCGT | nat gas | LNG (JKM) | BP-cogen | 100 |  | TUACCP5 |  | 1.2899 | 103.6403 | 4x 367 MW; 1x511 MW; Only cogen in Tuas (all the rest are in Jurong Island)
11 | Tuas Power Station | Tuas Power Generation Pte Ltd | Y | Y |  | 2005 | GRF | 735 | CCGT | nat gas | PNG (HH) | once-through | 100 | 0 | TUACCP3, 4 |  | 1.2899 | 103.6403
12 | Tuas Power Station | Tuas Power Generation Pte Ltd | Y | Y |  | 2002 | GRF | 735 | CCGT | nat gas | PNG (HH) | once-through | 100 | 0 | TUACCP1, 2 |  | 1.2899 | 103.6403 | TUACCP1 in 2001; TUACCP2 in 2002
13 | Tuas Power Station | Tuas Power Generation Pte Ltd | Y | Y |  |  | GRF | 600 | Oil-fired ST | oil | Crude (Dubai) | once-through | 100 | 0 | TUA OilST | 1x 600 MW | 1.2899 | 103.6403
14 | Sembcorp Cogen @ Banyan | SembCorp Cogen Pte Ltd | Y | Y |  | 2014 | GRF | 403.8 | Cogen CCGT | nat gas | LNG (JKM) | BP-cogen | 100 |  | SKACCP3 |  | 1.2587 | 103.6703
15 | Pulau Sakra Power Station | SembCorp Cogen Pte Ltd | Y | Y |  | 2001 | GRF | 785 | Cogen CCGT | nat gas | PNG (HH) | BP-cogen | 100 |  | SKACCP1, SKACCP2 |  | 1.2558 | 103.7023 | First cogen in SG
16 | Keppel Merlimau Cogen Power Station | Keppel Merlimau Cogen Pte Ltd | Y | Y |  | 2013 | GRF | 840 | Cogen CCGT | nat gas | LNG (JKM) | BP-cogen | 100 |  | KepMer CCP2 |  | 1.2824 | 103.6752
17 | Keppel Merlimau Cogen Power Station | Keppel Merlimau Cogen Pte Ltd | Y | Y |  | 2007 | GRF | 470 | Cogen CCGT | nat gas | PNG (HH) | BP-cogen | 100 |  | KepMer CCP1 |  | 1.2824 | 103.6752 | PNG import control didn't apply to this plant.
18 | PacificLight Power Plant | PacificLight Power Pte Ltd | Y | Y | Y | 2014 | GRF | 800 | CCGT | nat gas | LNG (JKM) | once-through | 100 | 0 | PLP Unit 1, 2 |  | 1.2824 | 103.7217 | First plant to use LNG. Uses up about 25% of imported LNG back in 2014
19 | Tuaspring Integrated Water & Power Project | Tuaspring Plant Pte Ltd | Y | N | N | 2016 | GRF | 395.7 | CCGT | nat gas | LNG (JKM) | once-through | 100 | 0 | TI CCP |  | 1.3031 | 103.6235 | Also a desalination plant
20 | Tuas South Incineration Plant | National Environment Agency | Y | N |  | 2000 | GRF | 131 | WtE ST | waste |  | dry-cooling | 150 | 10 | TSIP WtE |  | 1.2954 | 103.6213 | Two flue towers. Chose one closer to the Google Map address. Flue stack at 150 m (NEA) | Stack 150m
21 | Tuas Incineration Plant | National Environment Agency | Y | N |  | 1986 | GRF | 49.8 | WtE ST | waste |  | dry-cooling | 150 | 10 | TIP WtE |  | 1.3256 | 103.6349 | Brochure - consumes 35% of the elec it produces | Stack 150m
22 | Senoko Waste-to-Energy Plant | Senoko WTE Pte Ltd | Y | N |  | 1992 | GRF | 55 | WtE ST | waste |  | dry-cooling | 150 | 10 | SNK WtE |  | 1.4622 | 103.7947 | Near Senoko power station. The location near Sentosa is an office, not the plant.
23 | Keppel Seghers Tuas Waste-to-Energy Plant | Keppel Seghers Tuas WTE Pte Ltd | Y | N |  | 2009 | GRF | 22 | WtE ST | waste |  | dry-cooling | 100 | 10 | KepSeg WtE |  | 1.2973 | 103.6219 |  | Stack 100m
24 | Tembusu BMCC Plant | TP Utilities Pte Ltd | N | N |  | 2013 | GRF | 160 | Cogen Extraction ST | clean coal, biomass, nat gas | Coal (AU) | once-through | 100 | 0 | TMUC CCP |  | 1.2657 | 103.6765 | Cogen is for external industrial customers (e.g. pharma and petrochems). Part of the Tembusu Multi-Utilities Complex (TMUC), which produces steam, industrial water and demineralized water. No other info on 'biomass clean coal'. Coords are taken from the Google Maps address of TMUC Site 2 (cannot find flue tower). The plant operates a 101-MW extraction ST + 32.5 MW back-pressure ST (thus, HPR is adjustable). Cooling via sea water. The plant fires coal and biomass (woodchip + palm kernel) as its main fuel, with NG used as a backup).
25 | ExxonMobil Cogen Plant | ExxonMobil Asia Pacific Pte Ltd | N | N |  | 2012 | GRF | 332 | Cogen CCGT | nat gas | LNG (JKM) | BP-cogen | 100 |  | ExxMob CCP |  | 1.2799 | 103.7016 | For the ExxonMobil refineries (Jurong Island and Jurong; but maybe only for the Jurong Island refinery). These are actually two plants (220 MW + 140 MW) in 2016, but combined for simplicity. Total capacity is 380 MW, but less capacity must be licensed, to be consistent with EMA's total licensed capacity.
Note on D1: dkayanan: Main Power Producer vs Autoproducer (a facility that produces power but only secondary to its main business) As defined by EMA
Note on E1: dkayanan: Vested under the original Vesting Scheme of 2004 Src: Procedures for Calculating the Components of the Vesting Contracts v2.5, EMA
Note on F1: dkayanan: Not all LNG-fueled plants are vested under the LNG Vesting Scheme. Most likely, all LNG-vested plants came before non-vested LNG plants.
Note on G1: dkayanan: This is the latest commission year, after any plant upgrades (as opposed to when the first MWh was produced) Some power plants have units lumped (i.e. even if they were commissioned in different years). In such a case, then the commissioned year is the latest. EMA import control on PNG Announced 2006, cannot have new PNG import arrangements. Thus, plants commissioned ~2006-2013, prior to first LNG import, must have switched to LNG once the import started. Import control ceased in 2017.
Note on I1: dkayanan: Truly latest: - updated WtE plant registered capacities, which is significantly less than the nameplate due to significant houseloads (as seen from Tuas and Tuas South brochures). Latest -- Total reg capacity here is the same as EMA's, but the Autoproducer capacity is in excess of about 100 MW (conversely main producers lack 100 MW) ------------------------------------------------------------------------------- Where there are inconsistencies with info found, the EMA Energy Stats 2018 Table 2.3.1 was followed. Adjusting actual capacity to registered capacity Registered capacity <= actual MW capacity *PowerSeraya has 3100 MW of 3250 MW registered If there is not enough info on which plants are derated, then all stations are scaled by (registered MW/actual MW)
Note on J1: dkayanan: CCGT Combined cycle gas turbine OCGT Open cycle gas turbine ST Steam turbine
Note on L1: dkayanan: From May 2013 - end of 2017, EMA's import control on PNG was in effect -- all new gas turbines must source via LNG Assumption All CCGT plants prior to LNG coming to SG are supplied via PNG (i.e. assume that these are long-term contracts)
Note on M22: dkayanan: WtE brochures state cooling system
Note on M26: dkayanan: found in technical brochure that they have a BP & Ext-ST. The condensing unit shows a seawater cooling system.

## Plant Parameters
ID | Power Plant | Unit Name | Registered Capacity [MW] | Technology | Fuel ID* | Full Load Efficiency [%] | Efficiency rand var* | Efficiency Curve* | Cogen Total Efficiency | Min Stable Generation [MW] | Average Failures per year [yr-1] | Mean Time to Repair [wks] | MTTF [wks] | Alim [-]
0 | Senoko Power Station | SNK CCP 6, 7 | 862 | CCGT | LNG (JKM) | 48.7539 | eff_skewed | CCGT GT26 |  | 431 | 10.4414 | 0.62516 | 4.3687 | 0.87481
1 | Senoko Power Station | SNK CCP 4, 5 | 730 | CCGT | PNG (HH) | 62.2705 | eff_skewed | CCGT Best |  | 365 | 22.539 | 0.44772 | 1.8657 | 0.80647
2 | Senoko Power Station | SNK CCP 3 | 365 | CCGT | PNG (HH) | 58.4458 | eff_skewed | CCGT Best |  | 182.5 | 4.6941 | 1.5721 | 9.5361 | 0.85847
3 | Senoko Power Station | SNK CCP 1, 2 | 850 | CCGT | PNG (HH) | 60.3951 | eff_skewed | CCGT Best |  | 425 | 9.4419 | 0.63877 | 4.8837 | 0.88433
4 | Senoko Power Station | SNK OilST | 493 | Oil-fired ST | Crude (Dubai) | 37.07 | eff_skewed | ST sample |  | 246.5 | 6.0892 | 0.67544 | 7.8877 | 0.92112
5 | Pulau Seraya Power Station | PulSer CCP3, 4 | 740 | Cogen CCGT | LNG (JKM) | 35.0602 | eff_skewed | CCGT Typical | 83 | 370 | 14.0687 | 0.39852 | 3.3078 | 0.89247
6 | Pulau Seraya Power Station | PulSer CCP1, 2 | 732 | CCGT | PNG (HH) | 62.4879 | eff_skewed | CCGT GT26 |  | 366 | 5.9173 | 0.38208 | 8.4299 | 0.95664
7 | Pulau Seraya Power Station | PulSer OilST1 | 724 | Oil-fired ST | Crude (Dubai) | 34.2072 | eff_skewed | ST sample |  | 362 | 13.3972 | 0.64394 | 3.2481 | 0.83455
8 | Pulau Seraya Power Station | PulSer OilST2 | 724 | Oil-fired ST | Crude (Brent) | 34.021 | eff_skewed | ST sample |  | 362 | 9.414 | 0.80996 | 4.7289 | 0.85377
9 | Jurong Power Station | JRNG OCGT | 180 | OCGT | Crude (WTI) | 36.4345 | eff_skewed | CCGT Typical |  | 90 | 10.5269 | 0.27754 | 4.6758 | 0.94397
10 | Tuas Power Station | TUACCP5 | 405.9 | Cogen CCGT | LNG (JKM) | 38.4268 | eff_skewed | CCGT 4000F | 83 | 202.95 | 5.4682 | 0.37632 | 9.1594 | 0.96054
11 | Tuas Power Station | TUACCP3, 4 | 735 | CCGT | PNG (HH) | 61.8246 | eff_skewed | CCGT Typical |  | 367.5 | 8.6911 | 0.5604 | 5.4392 | 0.90659
12 | Tuas Power Station | TUACCP1, 2 | 735 | CCGT | PNG (HH) | 61.1739 | eff_skewed | CCGT Typical |  | 367.5 | 2.9812 | 3.4876 | 14.0032 | 0.8006
13 | Tuas Power Station | TUA OilST | 600 | Oil-fired ST | Crude (Dubai) | 35.396 | eff_skewed | ST sample |  | 300 | 21.0685 | 0.24908 | 2.2258 | 0.89936
14 | Sembcorp Cogen @ Banyan | SKACCP3 | 403.8 | Cogen CCGT | LNG (JKM) | 34.1887 | eff_skewed | CCGT 9F.05 | 83 | 201.9 | 4.9639 | 1.0736 | 9.4309 | 0.89779
15 | Pulau Sakra Power Station | SKACCP1, SKACCP2 | 785 | Cogen CCGT | PNG (HH) | 39.7868 | eff_skewed | CCGT Typical | 83 | 392.5 | 22.6268 | 0.38912 | 1.9154 | 0.83114
16 | Keppel Merlimau Cogen Power Station | KepMer CCP2 | 840 | Cogen CCGT | LNG (JKM) | 39.2209 | eff_skewed | CCGT GT26 | 83 | 420 | 7.0592 | 1.0768 | 6.3097 | 0.85423
17 | Keppel Merlimau Cogen Power Station | KepMer CCP1 | 470 | Cogen CCGT | PNG (HH) | 36.8061 | eff_skewed | CCGT 4000F | 83 | 235 | 14.8202 | 0.35185 | 3.1665 | 0.9
18 | PacificLight Power Plant | PLP Unit 1, 2 | 800 | CCGT | LNG (JKM) | 59.949 | eff_skewed | CCGT 701F |  | 400 | 22.9592 | 0.32364 | 1.9475 | 0.8575
19 | Tuaspring Integrated Water & Power Project | TI CCP | 395.7 | CCGT | LNG (JKM) | 61.0593 | eff_skewed | CCGT 701F |  | 197.85 | 18.9321 | 0.19186 | 2.5623 | 0.93034
20 | Tuas South Incineration Plant | TSIP WtE | 131 | WtE ST |  | 21.793 | eff_skewed | ST sample |  | 65.5 | 15.9885 | 0.41835 | 2.8429 | 0.87172
21 | Tuas Incineration Plant | TIP WtE | 49.8 | WtE ST |  | 18.111 | eff_skewed | ST sample |  | 24.9 | 12.9733 | 0.47432 | 3.5449 | 0.88199
22 | Senoko Waste-to-Energy Plant | SNK WtE | 55 | WtE ST |  | 23.0913 | eff_skewed | ST sample |  | 27.5 | 2.279 | 3.8459 | 19.0336 | 0.83191
23 | Keppel Seghers Tuas Waste-to-Energy Plant | KepSeg WtE | 22 | WtE ST |  | 19.9735 | eff_skewed | ST sample |  | 11 | 13.1223 | 0.34342 | 3.6302 | 0.91357
24 | Tembusu BMCC Plant | TMUC CCP | 160 | Cogen Extraction ST | Coal (AU) | 40 | eff_skewed | ST sample | 80 | 80 | 7.0739 | 0.99163 | 6.3796 | 0.86547
25 | ExxonMobil Cogen Plant | ExxMob CCP | 332 | Cogen CCGT | LNG (JKM) | 35.6638 | eff_skewed | CCGT GT26 | 83 | 166 | 12.9666 | 0.79479 | 3.2265 | 0.80235
Note on D1: dkayanan: Latest -- Total reg capacity here is the same as EMA's, but the Autoproducer capacity is in excess of about 100 MW (conversely main producers lack 100 MW) ------------------------------------------------------------------------------- Where there are inconsistencies with info found, the EMA Energy Stats 2018 Table 2.3.1 was followed. Adjusting actual capacity to registered capacity Registered capacity <= actual MW capacity *PowerSeraya has 3100 MW of 3250 MW registered If there is not enough info on which plants are derated, then all stations are scaled by (registered MW/actual MW)
Note on E1: dkayanan: CCGT Combined cycle gas turbine OCGT Open cycle gas turbine ST Steam turbine
Note on F1: dkayanan: keys are always case INsensitive, because they are used as keys metadata.ini
Note on G1: dkayanan: If combustion-based, pls. indicate the HHV efficiency.
Note on J1: dkayanan: Fixed to max efficiency
Note on K1: dkayanan: dummy param -- all 50%

## Random Seeds
ID | Power Plant | Unit Name | Full Load Efficiency | Start Online | UP Time Duration | DOWN Time Duration
0 | Senoko Power Station | SNK CCP 6, 7 | 209652396 | 398764591 | 924231285 | 1478610112
1 | Senoko Power Station | SNK CCP 4, 5 | 441365315 | 1537364731 | 192771779 | 1491434855
2 | Senoko Power Station | SNK CCP 3 | 1819583497 | 530702035 | 626610453 | 1650906866
3 | Senoko Power Station | SNK CCP 1, 2 | 1879422756 | 1277901399 | 1682652230 | 243580376
4 | Senoko Power Station | SNK OilST | 1991416408 | 1171049868 | 1646868794 | 2051556033
5 | Pulau Seraya Power Station | PulSer CCP3, 4 | 1252949478 | 1340754471 | 124102743 | 2061486254
6 | Pulau Seraya Power Station | PulSer CCP1, 2 | 292249176 | 1686997841 | 1827923621 | 1443447321
7 | Pulau Seraya Power Station | PulSer OilST1 | 305097549 | 1449105480 | 374217481 | 636393364
8 | Pulau Seraya Power Station | PulSer OilST2 | 86837363 | 1581585360 | 1428591347 | 1963466437
9 | Jurong Power Station | JRNG OCGT | 1194674174 | 602801999 | 1589190063 | 1589512640
10 | Tuas Power Station | TUACCP5 | 2055650130 | 2034131043 | 1284876248 | 1292401841
11 | Tuas Power Station | TUACCP3, 4 | 1982038771 | 87950109 | 1204863635 | 768281747
12 | Tuas Power Station | TUACCP1, 2 | 507984782 | 947610023 | 600956192 | 352272321
13 | Tuas Power Station | TUA OilST | 615697673 | 160516793 | 1909838463 | 1110745632
14 | Sembcorp Cogen @ Banyan | SKACCP3 | 93837855 | 454869706 | 1780959476 | 2034098327
15 | Pulau Sakra Power Station | SKACCP1, SKACCP2 | 1136257699 | 800291326 | 1177824715 | 1017555826
16 | Keppel Merlimau Cogen Power Station | KepMer CCP2 | 1959150775 | 930076700 | 293921570 | 580757632
17 | Keppel Merlimau Cogen Power Station | KepMer CCP1 | 80701568 | 1392175012 | 505240629 | 642848645
18 | PacificLight Power Plant | PLP Unit 1, 2 | 481447462 | 954863080 | 502227700 | 1659957521
19 | Tuaspring Integrated Water & Power Project | TI CCP | 1905883471 | 1729147268 | 780912233 | 1932520490
20 | Tuas South Incineration Plant | TSIP WtE | 1544074682 | 485603871 | 1877037944 | 1728073985
21 | Tuas Incineration Plant | TIP WtE | 848819521 | 426405863 | 258666409 | 2017814585
22 | Senoko Waste-to-Energy Plant | SNK WtE | 716257571 | 657731430 | 732884087 | 734051083
23 | Keppel Seghers Tuas Waste-to-Energy Plant | KepSeg WtE | 903586222 | 1538251858 | 553734235 | 1076688768
24 | Tembusu BMCC Plant | TMUC CCP | 1354754446 | 463129187 | 1562125877 | 1396067212
25 | ExxonMobil Cogen Plant | ExxMob CCP | 301492857 | 165035946 | 1883779156 | 576702667
Note on A1: dkayanan: Rand seeds are set as a function of the IDs for now
Note on D1: dkayanan: Full load efficiency adjustment rand var
Note on E1: dkayanan: Rand var that determines whether the plant starts online. This considers the limiting availability parameter of the plant.
Note on F1: dkayanan: UP / online time duration rand var
Note on G1: dkayanan: Down / repair time rand var

## Param Est
Decision -- maximize the overall efficiency, and then let n_e be selected from the reported range
Cogen Efficiencies
| high eff, max heat |  |  |  |  | high eff, max power
| ηoverall | ηe | ηh | HPR |  | ηoverall | ηe | ηh | HPR
CCGT | 83 | 34 | 49 | 1.4412 |  | 83 | 40 | 43 | 1.075
Ext-ST | 80 | 22 | 58 | 2.6364 |  | 80 | 40 | 40 | 1
| low eff, max heat |  |  |  |  | low eff, max power
| ηoverall | ηe | ηh | HPR |  | ηoverall | ηe | ηh | HPR
CCGT | 69 | 34 | 35 | 1.0294 |  | 69 | 40 | 29 | 0.725
Ext-ST | 60 | 22 | 38 | 1.7273 |  | 60 | 40 | 20 | 0.5
PPdb param
input here
|  | min | max
| MTTR [h] | 48 | 168 | [6 empty] | Methodology
| MTTR [wk] | 0.28571 | 1 |  | Fix these (min 2 days, max 1 wk) |  |  |  |  | 1) Assume MTTR froom 6h to 1wk (max repair time is thus 5wks)
| Max repair time [wk] | 1.4286 | 5 |  | The probability of getting fixed after 5*MTTR is << 1% |  |  |  |  | 2) Use the long-term availability for all of Sg fleet as the lower bound for Alim (~81%)
3) From MTTR and A, calculate MTTF, and then Ave failures per yr
| Availability [-] | 0.8 | 1 |  | Long-term availability for entire SG fleet at around 81%
compare with: FOR in US plants
Implement in calibration
| MTTF [wk] | 1.1429 | 999999 |  | Remember -- MTTF is the measure of reliability
| MTBF [wk] | 1.4286 | 1000000 | [6 empty] | 1) calib params:
| MTBF [yr] | 0.027397 | 19178.0822 | [7 empty] | MTTR [wks] | uniform, 2/7 to 1
| Ave Failure per yr | 36.5 | 5.2143e-05 | [7 empty] | Availability [-] | uniform, 0.8 to 0.99 | normal, mean=0.81 std dev=0.01
2) Solve the AF per yr param
3) Set MTTR and AF to PPdb
What if params are Alim and AF
|  | min | max
| Availability [-] | 0.8 | 0.95
| Ave Failure per yr | 2 | 24
Note on F22: dkayanan: data.gov power plant outage data
Note on S28: dkayanan: I changed my mind. I think the long-term ratio of outage cap/total cap per mo should be interpretted as a lower bound on the availability

## SG PP References
References
General
Singapore Energy Statistics 2018, EMA
Table 2.3.1 Capacity by generator of main producers
EMA
Licensed generation companies
Wikipedia
| List of power stations in SG | Stations, owners, fuel
Senoko Power Station
| Senoko Power Station (Wikipedia) | coordinates
| Senoko Power Station in the National Library | use of crude oil |  | Plant in Japan burns crude oil directly
Pulau Seraya and Jurong Power Station
Power Seraya
| Contact | coordinates
| Annual report '09-'10 | p34 -- Power Seraya has 2x370MW CCGT and 7x250MW Oil-fired ST
p34 -- New 800MW co-gen completed in Jul '10. Replaced 3 oil-fired ST
p 27 -- secured long-term LNG agreement with SLNG and BG Group for when SLNG Terminal completes in 2013 (signed 2010)
| Unveil of 800MW Co-Gen (2007) | 800 MW co-gen CCP has two units
Two existing CCPs to be converted to co-gen
All four co-gens at Pulau Seraya
| First in SG to offer Multi-Fuel Options (2005) | Existing 3x250 MW ST upgraded to use Orimulsion --> 3x250MW in Pulau Seraya are oil-fired ST
At this time, 6x250 MW oil ST more (3 of which replaced 2x400MW cogen in 2010) + 2x370 MW NG
| Media Resource | Actual MW
|  | 750 | Oil-fired ST
|  | 750 | Oil-fired ST w/ Orimulsion
|  | 740 | CCGT or w/o co-gen
|  | 800 | Cogen CCGT
|  | 210 | OCGT diesel
3250
Others
| Wiki - List of power stations in SG | Deduced that the 180 MW licensed diesel OCGT are at Jurong Power Stations; the rest
| Jurong gas plant | of the 2920 MW licensed capacity at Pulau Seraya station.
Tuas Power Station
Tuas Power
| Tuas Power Station | 5x CCGT
1x 600 MW ST
| Contact | coordinates
Wiki
| Tuas Power | All units are in one plant
Media
BT -- Tuas Power strts up its gas-fired cogen
Sembcorp power plants
Sembcorp
| Utilities brochure 2018 | Sakra cogen
Sakra energy from waste
Banyan cogen
104 MW PV
Actual capacity by fuel
Media
| ST -- Sembcorp opens $635 million co-gen plant in Jurong Island (Banyan) | 400 megawatts of power and 200 tonnes per hour of process steam
First cogen plant in SG (Pulau Sakra)
Keppel merlimau cogen
Keppel
| Keppel Merlimau Cogen Plant | 1300 MW cogen CCGT
PacificLight Power
Wiki
| PacificLight | 800 MW CCGT
Sources LNG
PacificLight |  | Siemens SGT5-4000F Gas Turbine
PacificLight launches the plant
Tuaspring Integrated Power and Water Plant
Hyflux (desalination co)
| Hyflux -- Tuaspring plant | 411 MW power + desalination plant
| Hyflux -- About Tuaspring | Sea water for CCGT cooling is then desalinated. Captured heat in sea water makes desalination easier.
All WtE plants
National Environment Agency
| Waste facilities in SG | Four WtE plants here
| WtE incineration plants | 150 m flue stack
| Tuas South Incineration brochure | 2x 66.3 MW ST
| Tuas Incineration brochure | 30 MW
NEA page has links to brochures of all(?) WtE plants
Others
| WtE Plants -- Public-Private parnership in SG | Author Loh Ah Tuan is former director-general of NEA
s11 outlines all WtE plants in SG
| About Senoko WtE | "WtE responsible for 2-3% of Sg elec needs" --> consistent with 'Others' category in fuel mix (2.9% in 2016)
Keppel-Seghers
| Keppel-Seghers WtE plants | Brochure for Senoko WtE and Keppel-Seghers Senoko WtE
Both were at least built by Keppel-Seghers
TP Utilities' BMCC plant in TMUC
Media
| ST -- SG's first coal plant | Fuel -- low-sulphur coal, biomass (palm kernel shells and woodchips), and NG or diesel
| Hyflux awarded contract for desalination plant in TMUC | BMCC is 160 MW
| ABB awarded an electrification contract | BMCC is 160 MW (2nd source)
ABB again
| TMUC inauguration speech | LNG
Tuas Power
| The Tembusu Multi-Utilities Complex | System efficiency up to 70% (heat + power)
Technical data but no values
| Contractor application | Technical data
ExxonMobil cogen
ExxonMobil
| 2017 - Comletes new 80 MW cogen plant | New 80 MW plant boosts cogen capacity to 440 MW -- thus, only up to 230 MW of 380 MW cogen capacity was licensed
Media
| New 80 MW plant is the third plant | ExxonMobil currently has three cogen plants
| ST -- generating power responsibly | Suggests all ExxonMobil's cogen facilities are CCGT
| On ExxonMobil new plant from 2010 | 220 MW cogen
More resources, not used
Singapore's largest power companies Mar 2017
On Senoko Energy, article in the Singapore Engineer, Mar 2012
Pasir Panjang Power Station 'A' decommissioned
Note on H127: p4 The BMCC cogeneration plant houses the following major energy equipment/facilities: - 2 x 450 T/H Coal and Biomass (Palm Kernel / Woodchip) fired Circulating Fluidized Bed (CFB) Boilers - 1 x 101MW Condensing (with 19 Bar extraction) Steam Turbine Generator (STG1) - 1 x 32.5MW LP (19 Bar) Backpressure (with HP 60 Bar and MP 42 Bar extraction) Steam Turbine Generator (STG2) - 3 x 200 T/H Nature Gas (NG) Backup Boilers - Seawater Intake Facilities (3 x 11,550 m3/h) - 3 x Coal Silo (3 x 28,500 m3) - Biomass Storage House (61,500 m3) - 66/22kV Switch House

## Cooling
Fuels
|  |  | Fuel | HHV [MJ/kg] | LHV [MJ/kg] | ratio | latent heat of combusion per unit HHV
|  |  | NG | 52.21 | 47.13 | 1.1078 | 9.73%
|  |  | Bit Coal (wet-basis) | 27.26 | 26.12 | 1.0436 | 4.182%
|  |  | HSFO | 42.2 | 39.5 | 1.0684 | 6.398%
Stack losses
Radiative, convective and other combustion losses
COMBUSTION
stack |  |  |  | Latent heat of combustion |  |  | Fuel-dependent as above
stack |  |  |  | Heat of exhaust gas |  |  | Technically dependent on firing conditions and flue gas temp; maybe we can get an ROT | Brayton cycle
|  |  |  | Other combustion losses |  |  | Misc combustion losses (e.g. coal ash) ~1%
OUTPUT
Electricity
Process heat
|  | HEAT REJECTION |  |  |  |  | Cooling-tech dependent
cooling tower |  |  |  | water vapor
cooling tower |  |  |  | heated air
outlet |  |  |  | heated water
OTHERS
|  |  |  | mech+elec+ stray |  |  | ~1%
Now, this template looks good. Time to fill-in some numbers.
Note on R14: dkayanan: Notice how exhaust T4 needs to be lower for higher efficiency